Fire Certificate

Inspection Checklist

CED FC ACS

### Air-Conditioning System

Name of Building:

| ###### A | #### AHU | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Smoke cut-off system provided within return air stream of AHU |  |  |
| ii | ### Activation of smoke-cut-off system shuts down AHU |  |  |
| iii | Manual reset provision for AHU |  |  |
| iv | No storage in AHU room |  |  |
| v | Smoke detector provided and tested in order |  |  |

| B | FIRE DAMPERS | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Fire Dampers are properly installed |  |  |
| ii | Motorised Fire dampers operate upon activation of auto fire alarm detectors |  |  |
| iii | No obstruction to dampers louver (blades) movement |  |  |
| iv | Access door for inspection of Fire dampers provided |  |  |
| v | Fire dampers of approved rating and with PSB label |  |  |

Date of inspection and testing of system:

CED FC ASCS

### Atrium Smoke Control System

Name of Building:

| S/No. | #### DETAILS:- | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Smoke detectors provided at the perimeter of the Atrium |  |  |
| ii | Separate manual reset switch provided |  |  |
| iii | Functions under Secondary supply provided |  |  |
| iv | Auto supply mode activated by fire alarm system (where applicable) under Secondary power supply |  |  |
| v | Manual activation provision installed |  |  |
| vi | System extraction air fan operate upon activation of fire alarm |  |  |
| vii | Smoke curtains operate upon activation of fire alarm |  |  |
| viii | Ventilation louvers operation by fire alarm and under secondary power supply are in order |  |  |
| ix | All fire scenarios where is / are designed under the engineered smoke control system has / have been tested |  |  |
| x | Air-condition cut-off upon activation of fire alarm |  |  |

Date of inspection and testing of system:

CED FC AFAS

# AUTOMATIC FIRE ALARM SYSTEM

Name of Building:

Name of Monitoring Company: 					Building Code No:

| S/No. | HEAT / SMOKE DETECTOR TEST | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Sufficient coverage |  |  |
| ii | Detector points not painted |  |  |
| iii | Detector points unobstructed |  |  |
| iv | System connected to monitoring company / 995 |  |  |
| v | ### Alarm signal transmission received by monitoring company |  |  |
| vi | Zone tested is indicated correctly on main-alarm panel |  |  |
| vii | ### Audible fault alarm & fault indication light provide at main-alarm panel |  |  |
| viii | #### Zoning diagram provided next to the main-alarm panel |  |  |
| ix | Zone tested is indicated correctly on sub-alarm panel |  |  |
| x | ### Audible fault alarm & fault indication light provide at sub-alarm panel |  |  |
| xi | #### Zoning diagram / mimic panel provided next to the sub-alarm panel |  |  |
| xii | #### Alarm bells in operational condition |  |  |
| xiii | #### Alarm general sounding throughout the building |  |  |

Date of inspection and testing of system:

CED FC AFSS

# AUTOMATIC FIRE SUPPRESSION SYSTEM FOR COOKING HOOD

Name of Building:

| # A | ## GENERAL | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### System connected to Main / Sub Fire Alarm Panel |  |  |
| ii | #### Automatic cut-off device for gas fuel supply provided |  |  |
| iii | #### Emergency manual release for extinguishing agent provided |  |  |
| iv | #### Sign “IN CASE OF FIRE – PULL TO RELEASE”CALL 995 is provided |  |  |

| ## B | ###### CYLINDER FOR EXTINGUISHING AGENT | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | PSB Approved label provided |  |  |
| ii | Rigidly mounted |  |  |
| iii | Service by fire safety work contractor (competent personnel) |  |  |
| iv | Date of service |  |  |

| ## C | ## NOZZLE & PIPE WORKS | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Rigidly mounted |  |  |
| ii | ### Free of grease (internal & external) |  |  |
| iii | Free of obstruction |  |  |
| iv | Double layer provided |  |  |

| ##### D | HEAT ACTIVATING DEVICE | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Fusible link enclosed in piping |  |  |
| ii | Free of obstruction |  |  |
| iii | Free of grease |  |  |
| iv | Properly installed |  |  |
| v | #### Ensure in functioning condition (conduct simulated test) |  |  |

Date of inspection and testing of system:

CED FC CPSES

### Car Park Smoke Extract System

Name of Building:

| S/No. | #### DETAILS:- | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Intake / discharge location with at least 5m separation |  |  |
| ii | Exhaust discharge directed to external |  |  |
| iii | Connected to secondary power supply & fire alarm system |  |  |
| iv | Failure of the Exhaust Fan will cut off the corresponding supply fan |  |  |

Date of inspection and testing of system:

CED FC DRS

# DRY RISER SYSTEM

Name of Building:

DRY RISER:	size 2 way (100mm) No.			     /4 way (150mm) No.

| A | #### Breeching Inlet | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Inlet housed in glass fronted protective enclosure |  |  |
| ii | Properly installed / secured |  |  |
| iii | Clear of Obstruction |  |  |
| iv | About 0.76m above finished floor level |  |  |
| v | Labelled “DRY RISER INLET” and differentiated |  |  |
| vi | Inlet painted in yellow colour |  |  |

| B | #### Riser | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ##### Not passing through unprotected area / Fire rated |  |  |
| ii | Air release valve provided |  |  |
| iii | Earthling provided |  |  |

| C | #### Landing Valve | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | 0.76m to 1m above finished floor level |  |  |
| ii | Condition of hand wheel satisfactory |  |  |
| iii | Blank Cap provided |  |  |
| iv | Strapped and padlocked in closed position |  |  |
| v | Labelled / Numbered |  |  |
| vi | Clear of Obstruction |  |  |
| vii | Landing valve painted in yellow colour |  |  |

| ###### D | ## Testing of Hydrostatic Pressure | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Pressure constant at 200 PSI for 2 hrs |  |  |
| ii | Air release valve functioning |  |  |

Date of inspection and testing of system:

CED FC ESCS

### engineered Smoke Control System

Name of Building:

| S/No. | #### DETAILS:- | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Separate manual reset switch provided |  |  |
| ii | Functions under secondary supply provided |  |  |
| iii | Auto supply mode activated by fire alarm system under normal power supply |  |  |
| iv | Auto supply mode activated by fire alarm system under secondary power supply |  |  |
| v | Manual activation provision installed |  |  |
| vi | Air exhaust fan operate upon operation of fire alarm |  |  |
| vii | Air condition system cut-off upon activation of system |  |  |
| viii | Smoke curtain operate upon activation of system |  |  |

Date of inspection and testing of system:

CED FC HRS

### hose reel SYSTEM (with pump)

Name of Building:

| ##### A | Hose | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Non-kinking reinforced rubber |  |  |
| ii | Length of hose (30m) |  |  |
| iii | Nozzle condition satisfactory |  |  |
| iv | Locking device provided in-order |  |  |
| v | Condition of stop cock satisfactory |  |  |
| vi | Clear of obstruction |  |  |
| vii | Labelling provided for cabinet |  |  |
| viii | Labelling provided for instruction signage |  |  |
| ix | No locking device provided |  |  |

| B | Testing | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | No Leakage detected |  |  |
| ii | 6m throw achievable or flow rate of 0.4 litre / sec |  |  |

| ###### C | ###### Pump | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | #### Pump can be manually tested |  |  |
| ii | Auto changeover from normal to secondary power supply |  |  |
| iii | Auto changeover from duty to standby pump operation in order |  |  |
| iv | Differentiated |  |  |

Date of inspection and testing of system:

CED FC LIFT

### Lift

Name of Building:

| (No. of Passenger Lift ______________ Cargo Lift ______________ Fire Lift ______________) |  |  |  |
| --- | --- | --- | --- |
| A | Passenger and Fire Lift | #### * Status of Inspection |  |
|  |  | Yes | #### N.A. |
| i | Lift homing under fire alarm activation in order (Clause 13.1.3) |  |  |
| ii | Lift homing under secondary power supply (Clause 13.1.2) |  |  |
| iii | Warning notice for fire situation provided (Clause 13.1.8) |  |  |
| iv | PSB (SISIR) approved EBOPS provided (Clause 12.3) |  |  |
| v | #### EBOPS supply to lift car bell, lighting and fan in order |  |  |
| vi | #### Lift differentiated with numbers |  |  |
| vii | Storey Numbering for lift lobbies provided |  |  |
| viii | Lifts home at designated floor |  |  |

| B | Fire Lift (Size & Capacity __________________________) | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Lift travel from ground to top level within 1 minute |  |  |
| ii | Fire lift operated under fire switch in order |  |  |
| iii | Labelled “FIRE LIFT” |  |  |
| iv | Fire switch properly enclosed in labelled glass fronted cover |  |  |
| v | No combustible furnishing |  |  |

Date of inspection and testing of system:

CED FC OSF

OTHER SYSTEMS AND FIXTURES

##### 1)	HOSE REEL (without pump)

| ##### A | Hose | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Non-kinking reinforced rubber |  |  |
| ii | Length of hose (30m) |  |  |
| iii | Nozzle condition satisfactory |  |  |
| iv | No locking device provided |  |  |
| v | Condition of stop cock satisfactory |  |  |
| vi | Clear of obstruction |  |  |
| vii | Labelling provided for cabinet |  |  |
| iv | Labelling provided for instruction signage |  |  |

| B | Testing | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | No Leakage detected |  |  |
| ii | 6m throw achievable/0.4 l/sec |  |  |

Date of inspection and testing:

2)	PORTABLE FIRE EXTINGUISHER

| S/No | Details: | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Properly hung on bracket |  |  |
| ii | Clear of obstruction |  |  |
| iii | Service by licensed contractor |  |  |
| iv | PSB label |  |  |
| v | Date of service |  |  |

Date of inspection:

CED FC OSF

3)	MANUAL ALARM SYSTEM (CALL POINT)

| S/No | Details: | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | The colour for all fire alarm panels, bell ,conduit and trunking are painted red |  |  |
| ii | Clear of obstruction |  |  |
| iii | Fire alarm zoning diagrams provided near fire alarm panel |  |  |
| iv | General sounding throughout the building |  |  |
| v | Located about 1.4m from floor level |  |  |
| vi | Alarm bell in operational condition |  |  |
| vii | The fire alarm sounding distinguishable from any other alarm system |  |  |
| viii | Audible fault alarm & fault indication light provided at sub / main panel |  |  |
| ix | Zone tested is indicated correctly on the fire alarm main / sub panel |  |  |
| x | “IN CASE OF FIRE CALL 995” signage provided |  |  |

Date of inspection and testing:

#### 4)	EXIT SIGN AND EMERGENCY LIGHTING

| A | Exit Sign / Exit Directional Sign | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | #### Exit Sign adequately provided along :- - Staircase - Escape Routes - Public Area |  |  |
| ii | Exit Sign Visible |  |  |
| iii | Directional Exit Sign provided where necessary |  |  |
| iv | Exit Sign operation in order |  |  |
| v | Exit Sign connected to secondary power supply tested in order |  |  |
| vi | Exit sign complied with CP 19 colour code (green and white combination) |  |  |

CED FC OSF

| B | Emergency Lighting | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Emergency Lighting provide along :- - Staircase - Escape Route - Public Area - Essential plant rooms |  |  |
| ii | Automatic operation tested in order |  |  |
| iii | Emergency lighting provided is sufficient |  |  |
| iv | Identification ( Cl 7.8 CP 19 ) |  |  |
| v | Emergency Lighting connected to secondary power supply |  |  |

Date of inspection and testing:

###### 5)	fire door and exit door

| A | Fire Door | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Fire door installed at follow location are in order - Staircases - Escape Routes - Public Area |  |  |
| ii | Fire doors provided with PSB label |  |  |
| iii | Swing of door in direction of escape |  |  |
| iv | No stopper detected |  |  |
| v | Self-closer provided |  |  |
| vi | Doors are closed fitting |  |  |
| vii | Clear of obstruction |  |  |
| viii | Panel above the door same rating as the wall |  |  |
| ix | No locking device for doors passing to the fire fighting staircase |  |  |
| x | Viewing glass panel at fire rated door does not exceed 650 cm2 |  |  |

CED FC OSF

| B | Exit Door | * Status of inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Doors unlocked during operating hour |  |  |
| ii | Clear of obstruction |  |  |

Date of inspection:

6)	DUCT RISER

| S/No | Details: | * Status of inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Fire stopped accordingly |  |  |
| ii | Protected by fire-resisting enclosure |  |  |
| iii | No Storage |  |  |

Date of inspection:

7)	STAIRCASE (ENCLOSED 			 OPEN 			)

| S/No | Details: | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Standard Stairway Numbering System provided |  |  |
| ii | Clear of obstruction |  |  |
| iii | No combustible furnishing |  |  |
| vi | Fully compartmented |  |  |
| v | Service pipe (gas, oil and ventilation) other that water pipe not passing through protected staircase, lobbies area |  |  |

Date of inspection:

8)	EXTERNAL FIRE FIGHTING ACCESS OPENING

| S/No | Details: | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Clear of obstruction internal and external |  |  |
| ii | (Red or Orange) External marking provided |  |  |
| iii | Signage “Fire Fighting Access – Do Not Obstruct” provided |  |  |
| vi | Readily open from inside and outside |  |  |

Date of inspection:

CED FC OSF

9)	THEATRE

| A | AUDITORIUM | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Approved occupant load |  |  |
| ii | Seats firmly fixed |  |  |
| iii | Exit doors provided with panic bolts |  |  |
| iv | Hose reel tested in order |  |  |
| v | Exit signs in good working order |  |  |
| vi | Exit signs provide with secondary power supply Complying with CP 19 |  |  |
| vii | Beacon light operation in order |  |  |
| v | Emergency lighting auto changeover tested in Order |  |  |

| B | STAGE | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| i | Provided with self-closing fire rated door |  |  |
| ii | ### Fire extinguisher provided |  |  |
| iii | No storage |  |  |
| Iv | Smoke curtain provided |  |  |

| C | PROJECTION ROOM | * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | N.A. |
| I | Provided with self-closing fire rated door |  |  |
| Ii | ### Fire extinguisher provided |  |  |
| Iii | Emergency lighting tested in order |  |  |
| Iv | Emergency message slide / public address system tested in order |  |  |
| V | Shutter operated smoothly / fire rated glass Installed |  |  |
| Vi | No smoking sign displayed |  |  |

Date of inspection and testing:

CED FC PS

### Pressurisation System

Name of Building:

Location of Fans

Fans supply to (staircase / lift lobby / corridor / 								)

| S/No. | #### DETAILS:- | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Separate manual reset switch provided |  |  |
| ii | Fan operation at high speed under fire alarm (if single) |  |  |
| iii | Both fans operating under fire alarm (if double) |  |  |
| iv | Fan operating upon secondary power supply (Fire mode) |  |  |
| v | Fan in operation can only be stopped manually |  |  |
| vi | Average air velocity not less than 1 m/s |  |  |
| vii | Force require to open any door is not more than 110 N |  |  |
| viii | Independent system for smoke lobby / protected corridor connected to secondary power supply |  |  |

Date of inspection and testing of system:

CED FC PHS

# PRIVATE HYDRANT SYSTEM

Name of Building:

HYDRANT No.:

| A | #### HYDRANT | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Rigidly mounted on ground |  |  |
| ii | Cover for spindle chamber visible |  |  |
| iii | Spindle depth not more than 1 metre |  |  |
| iv | Blank cap provided |  |  |
| v | Spindle chamber and Hydrant clear of obstruction |  |  |
| vi | Hydrant painted with yellow colour band |  |  |

| ###### F | #### Testing of STATIC PORESSURE AND FLOW RATE |  |  |  |
| --- | --- | --- | --- | --- |
| i | HYDRANT NO. | STATIC PRESSURE | FLOW RATE IN L/SEC | REMARKS |

Date of inspection and testing of system:

CED FC SGS

# STANDBY GENERATOR SET

Name of Building:

Location of Standby generator set(s):

| # A | ###### GENERATOR OPERATION | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| # i | Automatically changeover within 15 sec. |  |  |
| # ii | #### Smoke exhaust in-order |  |  |
| # iii | #### No storage |  |  |

| # B | GENERATOR SET TESTED ON FULL LOAD - SUPPLY TO THE FOLLOWING SYSTEMS SIMULTANEOUSLY |  |  |  | #### * Status of Inspection |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Yes | #### N.A. |
| i | Emergency lighting |  | - | Common corridor / staircases |  |  |
|  |  |  | - | #### Fire pump rooms |  |  |
|  |  |  | - | #### Generator / switch rooms |  |  |
|  |  |  | - | #### Illuminated exit / directional exit signs |  |  |
| ii | Fire pump system |  | - | Wet riser main pump |  |  |
|  |  |  | #### - | #### Wet riser transfer pump |  |  |
|  |  |  | #### - | #### Sprinkler main pump |  |  |
|  |  |  | #### - | #### Sprinkler transfer pump |  |  |
|  |  |  | #### - | #### Hose reel pump |  |  |
| iii | Lift system |  | - | Homing of lifts |  |  |
|  |  |  | - | Operation of fire lift |  |  |
| iv | #### Mechanical |  | #### - | #### Atrium fan |  |  |
|  | #### Ventilation system |  | #### - | #### Engineered smoke control system fan |  |  |
|  |  |  | #### - | #### Pressurisation fan |  |  |
|  |  |  | #### - | #### Car park smoke extract system fan |  |  |
|  |  |  | #### - | #### Fire pump room fan |  |  |
|  |  |  | #### - | #### Smoke stop lobby |  |  |
| v | Public addressing system |  |  |  |  |  |

Date of inspection and testing of system:

CED FC VCS

### VOICE COMMUNICATION SYSTEM

Name of Building:

| A | One-way Communication | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Operational test in order |  |  |
| ii | Standby battery provided |  |  |
| iii | Secondary power supply provided |  |  |
| iv | Over riding switch provided at Fire Command Center (FCC) |  |  |

| B | Two-way communication | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Operation tested in order |  |  |
| ii | Standby battery provided |  |  |
| iii | Secondary power supply provided |  |  |
| iv | Provided at Strategic Location |  |  |
| v | To label & colour in red |  |  |
| vi | 1.5m above the floor |  |  |
| vii | Operational test is indicated correctly at panel in FCC |  |  |

Date of inspection and testing of system:

CED FC WRS

# WET RISER SYSTEM

Name of Building:

WET RISER: Size: 						Nos.

| ## A | ###### BREECHING INLET | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Inlet housed in glass fronted protective enclosure |  |  |
| ii | Properly installed / secured |  |  |
| iii | Clear of Obstruction |  |  |
| iv | About 0.76m above finished floor level |  |  |
| v | Labelled “WET RISER INLET” and differentiated |  |  |

| ###### B | RISER | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Earthing provided |  |  |
| ii | Air release valve provided |  |  |
| iii | Not passing through unprotected area / fire rated |  |  |

| ## C | ###### LANDING VALVES | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | 0.76m to 1m above finished floor level |  |  |
| ii | Condition of hand wheel satisfactory |  |  |
| iii | Blank Cap provided |  |  |
| iv | Strapped and padlocked in closed position |  |  |
| v | Labelled / Numbered |  |  |
| vi | Clear of Obstruction |  |  |

| ## D | ## WATER TANK | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Overflow pipe provided |  |  |
| ii | Inflow pipe provided |  |  |
| iii | Compartmented |  |  |

| ## E | ## TRANSFER PUMP | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Pump can be manually tested |  |  |
| ii | Auto changeover from normal to secondary power supply in order |  |  |
| iii | Auto changeover from duty to standby pump operation in order |  |  |

| ## F | ## PUMP OPERATION CONTROL PANEL | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Pump numbering tallied with actual control panel indicator |  |  |
| ii | Clear from drain off test facilities |  |  |
| iii | Power to pump indicator light “on” |  |  |
| iv | Sheltered / weather proof |  |  |

FSSD FC (02 - 02)

| G | PUMP | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | #### Auto changeover from normal to secondary power supply in order |  |  |
| ii | Auto changeover from duty to standby pump operation in order |  |  |
| iii | All valves to pumps kept strapped and padlocked |  |  |
| iv | Top most landing valve fully opened (under pump gravity feed) and flow rate in order |  |  |
| v | Discharge for the test drain pipe provided |  |  |

| H | TESTING OF STATIC PRESSURE AND FLOW RATE | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Running pressure in between 3.5 bar to 5.5 bar |  |  |
| ii | #### Static pressure less than 8 bar |  |  |

| I | #### PUMP ROOM VENTILATION | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Mechanical ventilation fan provided are in working order |  |  |

### FLOW RATE TEST ON WET RISER SYSTEM

| STACK NO | STOREY TESTED | STATIC PRESSURE | FLOW RATE IN L/SEC | PUMP(P)/ GRAVITY (G) FEED | REMARKS |
| --- | --- | --- | --- | --- | --- |

Date of inspection and testing of system:

CED FC SPRS

# AUTOMATIC SPRINKLER SYSTEM

Name of Building:

Storey serve:

| ## A | ###### LAYOUT | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Sufficient Coverage |  |  |
| ii | Sprinkler Head Obstructed |  |  |
| iii | Cut-off sprinkler head provided (toilets, staircase landings, etc) |  |  |
| iv | Protective guard provided for sprinkler head (if applicable) |  |  |

| ###### B | BREECHING INLET | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Clear of obstruction |  |  |
| ii | Inlet housed in protective enclosure |  |  |
| iii | Labelled “SPRINKLER BREECHING INLET” |  |  |
| iv | 2/4 way inlet provided |  |  |
| v | About 0.76m above surrounding road or pavement level |  |  |
| vi | Rigidity supported |  |  |
| vii | Inlet connected to main sprinkler Tank/Break Tank |  |  |

| ## C | ###### SPRINKLER TANK | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Access panel and ladder provided |  |  |
| ii | Overflow pipe provided |  |  |
| iii | Compartmented |  |  |

| ## D | ## TRANSFER PUMP | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Pumps can be manually tested |  |  |
| ii | Inflow pipe provided |  |  |
| iii | Compartmented |  |  |

| ## E | ## TRANSFER PUMP | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Pump can be manually tested |  |  |
| i | Auto changeover from normal to emergency power supply in order |  |  |
| iii | Auto changeover from duty to standby pump operation in order |  |  |

| ## F | ## PUMPS | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | ### Auto change over from duty to standby pumps operation in order |  |  |
| ii | Auto change over from normal to emergency power supply in order |  |  |
| iii | Differentiated |  |  |
| iv | Discharge for the test drain pipe provided |  |  |
| v | Pressure gauge provided |  |  |
| vi | Cut in pressure tested in orders |  |  |

| G | SPRINKLER CONTROL VALVE | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | #### Gong provided in order |  |  |
| ii | Labelled to indicate storey served |  |  |
| iii | Strapped and padlocked in open position |  |  |
| iv | Approximately 1m high |  |  |
| v | Clear of obstruction |  |  |
| vi | Location plate with label provided at the access door (if enclosed) |  |  |

| H | SPRINKLER PIPE | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Not passing through unprotected area/fire rated |  |  |
| ii | #### Not encased by concrete |  |  |

| I | #### PUMP INDICATOR PANEL | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Pump numbering tallied with actual operation |  |  |
| ii | Selector switch in Auto position |  |  |
| iii | Power to pump indicator light “ON” |  |  |

| J | #### DRAIN TEST | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Drain off at control valve/pump room |  |  |
| ii | Cut-in pressure of pumps not less than 80% of running pressure |  |  |

### (K)	DRAIN OFF TEST RESULT

| Control Valve |  | Installed Pressure | Duty Pump |  | Standby Pump |  | REMARKS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Location | Coverage |  | Cut-in Pre | Running Pre | Cut-in Pre | Running Pre |  |

Date of inspection and testing of system:

### CED FC PFP

### PASSIVE FIRE PROTECTION TO STRUCTURAL STEEL COLUMNS AND BEAMS

Name of Building:

| A | Intumescent Paint provided with signage | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | Name of Supplier |  |  |
| ii | Fire resistance rating of the intumescent paint |  |  |
| iii | Date of painting |  |  |
| iv | Expected date of re-painting |  |  |
| v | Caution notice: “Caution: No other paint/coating shall be applied to the Surfaces of the structural steel members protected by the intumescent paint system” |  |  |
| vi | No storage of highly flammable/combustible materials within the vicinity of Structural steel members protected by the intumescent paint |  |  |

| B | Dry Board | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | No alterations and additions work to the dry board (unless approval is obtained) |  |  |
| ii | Check for any damages or tempering to the dry board |  |  |

| C | Spray-On Material | #### * Status of Inspection |  |
| --- | --- | --- | --- |
|  |  | Yes | #### N.A. |
| i | No alterations and additions work to the spray-on material (unless approval is obtained) |  |  |
| ii | Check for any damages or tempering to the spray-on material |  |  |

Date of inspection and testing of system: ______________________________________