## BP2 Main Page
DETERMINATION OF NO OF PERSONS PROVIDED WITH MEANS OF ESCAPE AT EACH NON-RESIDENTIAL STOREY
Proposal:
Storey:
Instruction: | One copy of this form is to be submitted for each *non-residential storey/typical storey for every new building & for amendments or alterations & additions where there is an increase in occupant load. (Separate calculations are needed for cinemas, auditoriums and the like)
1 | The occupant load of this storey based on the floor area of: |  |  | sq m.
| The applicable rates of Table 1.2A of the Code of Practice for Fire Precautions in Buildings 2013 is: |  | 0 | persons.
(Detail calculations shall be attached. Please use Form FSB-BP3)
2 | No of persons provided with means of escape for this storey is: |  | 0 | persons.
I confirm that the means of escape provided for this storey comply with the provisions of the Code of Practice for Fire Precautions in Buildings 2013.
Name of Qualified Person's Firm
Note: Filling in this form may take more than 15 minutes
Qualified Person's name & signature |  | Date
Note on C31: Enter the name of Qualified Person submitting this calculations. He/She needs to sign after this sheet is printed out
Note on D7: Enter the project title of the proposal
Note on D12: Enter the storey or typical storey no. for the purpose of this calculations
Note on F25: The name of the Qualified Person's company
Note on H31: Date of signature
Note on J16: Enter the floor area of this floor for the purpose of this calculations

## BP2 Calculations
DETERMINATION OF NO OF PERSONS PROVIDED WITH MEANS OF ESCAPE AT EACH NON-RESIDENTIAL STOREY
PROPOSAL:
Note: For 1st storey with direct exit to external without relying on the protected staircase, columns no. 2a, 3a & 4a shall be left blank.
(1) Storey occupancy (eg 5th storey office) | (2) Exit located or Idendification |  | (3) Clear width (m) |  | (4) Units of Width (1/2 m each)(Exit Rate - Persons/Unit Width) |  |  |  | (5) Exit capacity (No of persons) |  | (6) No of persons provided with means of escape (the smallest) of 5a & 5b
| (2a) Stairs (eg stair A) | (2b) Exit doors (eg door to stair A) | (3a) Stairs (eg 1.8) | (3b) Exit doors (eg 1.4) | (4a) Stairs |  | (4b) Exit doors (80) |  | (5a) Stairs | (5b) Exit doors
[5 empty] | Unit of Width | Persons per Unit Width (eg 60) | Unit of Width | Persons/Unit Width (eg 80)
[10 empty] | Total: | 0
Qualified Person's name and signature |  |  |  | Date
Note on A13: Enter the storey or typical storey no. and the occupancy
Note on B13: Enter the name of each staircase (eg. Stair A) Please leave this column blank if the exit is not through a staircase
Note on C13: Enter the door to the particular staircase or directly to the external space of the building
Note on D13: Enter the clear width of the staircase. Please leave this column blank if the exit is not through a staircase
Note on E13: Enter the clear width of the staircase door or exit door opens directly to the external of the building
Note on G13: Column (iv) of Table 2.2A. Please leave this column blank if the exit is not through a staircase
Note on I13: Column (iv) of Table 2.2A

## BP3
PROPOSAL:
OCCUPANT LOAD CALCULATION FOR
Item No. | Usages | Floor Area (m2) | Area of occupied floor space per person (m2) | No of persons | Remarks
|  |  | Total: | 0
Qualified Person's name & signature |  |  | Date
Note on A9: Enter item no.
Note on B9: Enter usage of the functional space
Note on C9: Enter area of the space
Note on D9: Enter occupancy load in the relevant Schedule of Table 1.2A

## BP4
INFORMATION ON UNPROTECTED OPENINGS
(CLAUSE 3.5.3 OF THE CODE OF FIRE PRECAUTIONS IN BUILDING 2013)
PROPOSAL:
BUILDING ELEVATION
Dimemsions of enclosing Rectangle (as defined in Appendix 'B' Clause 3.5.3) | Width (m)
Height (m)
Area (m2)
Unprotected Opening | Area provided (m2)
Percentage over enclosing rectangle (%)
Setback | Required (m)
Actual provision (m)
Fire rating of external wall required
Material of external wall
Fire protection system required
Qualified Person's name & signature |  | Date
Note on C14: Enter the elevation (eg North Elevation)
Note on C15: Width of enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on C16: Height of the enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on C18: The aggregate unprotected opening provided in sq m on this elevation
Note on C20: See relevant column of Table in Appendix 'B' to Clause 3.5
Note on C21: Actual provisions shown on drawings
Note on D14: Enter the elevation (eg South Elevation)
Note on D15: Width of enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on D16: Height of the enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on D18: The aggregate unprotected opening provided in sq m on this elevation
Note on D20: See relevant column in Table in Appendix 'B' to Clause 3.5
Note on D21: Actual provisions shown on drawings
Note on E14: Enter the elevation (eg East Elevation)
Note on E15: Width of enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on E16: Height of the enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on E18: The aggregate unprotected opening provided in sq m on this elevation
Note on E20: See relevant column in Table in Appendix 'B' to Clause 3.5
Note on E21: Actual provisions shown on drawings
Note on F14: Enter the elevation (eg West Elevation)
Note on F15: Width of enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on F16: Height of the enclosing rectangle in metres round up to the nearest row in the relevant Table
Note on F18: The aggregate unprotected opening provided in sq m on this elevation
Note on F20: See relevant column in Table in Appendix 'B' to Clause 3.5
Note on F21: Actual provisions shown on drawings

## Table 2.2A
TABLE 2.2A DETERMINATION OF EXIT REQUIREMENT
(i) Type of Occupancy | (ii) Max Travel distance (m) (One-way Escape) |  | (iii) Max Travel Distance (m) (Two-way Escape) |  | (iv) Capacity No of persons per unit of width (x) |  |  |  | (v) Min Width (m) |  | (vi) Max Dead End (m)
[5 empty] | Door opening (c), (e) |  | (f) | (d) | Stairs | Corridors | Corridors
| Unsprin- klered | Sprin- klered | Unsprin- klered | Sprin- klered | To outdoors at ground level | Other exit & corridor doors | Stair- cases | Ramps corridors exits passage- ways |  |  | Unsprin- klered | Sprin- klered
High hazard | 10 | 20 | 20 | 35 | 50 | 40 | 30 | 50 | 1 | 1.2 | 15 | 20
Industrial building (factories, workshops, godowns/warehouse) | 15 | 25 | 30 | 60 | 100 | 80 | 60 | 100 | 1 | 1.2 | 15 | 20
Shops | 15 | 25 | 45 | 60 | 100 | 80 | 60 | 100 | 1 | 1.2 | 15 | 20
Offices | 15 | 30 | 45 | 75 | 100 | 80 | 60 | 100 | 1 | 1.2 | 15 | 20
Places of public resort & carparks | 15 | 25 | 45 | 60 | 100 | 80 | 60 | 100 | 1(h) | 1.2(h) | 15 | 20
Schools & educational buildings | 15 | 25 | 45 | 60 | 100 | 80 | 60 | 100 | 1 | 11/2(a) | 15 | 20
Hospitals | 15 | 25 | 30 | 45 | 30 | 30 | 15 | 30 | 1 | 2(b) | 15 | 20
Hotels, boarding houses,service apartments,hostels,backpackers hotels,dormitories | 15 | 20 | 30 | 60 | 60 | 50 | 45 | 50 | 1 | 1.2 | 15 | 20
Blocks of flats/maisonettes (k) | 15(g) 20(j) | 30(g) 40(j) | 30 45(j) | 75 | 50 | 40 | 30 | 50 | 1(I) | 1.2 | 15 | 20
Detached, semi-detached & terrace houses, including townhouses | NR | NR | NR | NR | NR | NR | NR | NR | 0.9 | 0.9 | NR | NR
NR = No requirements Maximum direct distance = 2/3 x maximum travel didtance ... See Cl.1.2.18
(x) Unit of width = 0.5 metres.
(a) Applies to corridors serving classrooms. Other corridors shall have a minimum width of 1.2 metre.
(b) Applies to corridors serving patients. Other corridors shall have a minimum of 1.2 metre
(c) See Cl.2.3.9.
(d) See Cl.2.3.8
(e) Where a door opening is divided by mullions into two or more door openings, each such Openings shall be measured separately in computing the number of units of exit width.
(f) See Cl.2.2.15 regarding reduction of exit provision.
(g) For travel distance in single staircase flats ... See Cl.2.4.
(h) Refer to Cl.2.8.2
(i) Staircase within maisonette serving as an internal access to be at least 0.9 m width.
(j) Applies to external corridor ... See Cl.2.4.9.
(k) Measurement of travel distance is from the residential unit door to exit ... See Cl 2.4.7